INTERNATIONAL ELECTROTECHNICAL COMMISSION SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

TITLE: Draft Revision to Decision Sheet DS 2012/005 - Inclusion of an IP rating

as part of the marking and certificate

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

As a result of discussion held during the TC31 WG22 October 2015 meeting, concerning the need to keep marking for two different IP situations separate, it was agreed by the WG that ExTAG DS 2012/005 be revised. The following document proposes a modification to reflect that discussion.

Please submit comments using the attached comments table by -

2015 11 19 to

Christine Kane

If there are no comments received the document will be forwarded for publication.

- Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

| Member Body | Clause/ Sub-clause | Paragraph Figure/ Table | Type of comment General/ technical/ editorial | COMMENTS | Proposed change | Observation (to be completed by the originator) |
| --- | --- | --- | --- | --- | --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-0:2011 IEC 60079-0:2007 IEC 61241-0:2004 | Clauses: 29 29 29 |  |
| --- | --- | --- |
| Subject: Inclusion of an IP rating as part of the marking and certificate Status of document: Approved | Key words: - IP rating - Marking - Certificate | # Date: 151020 Originator of proposal: UL Modification proposed by SGS Baseefa to DS 2012/005 following discussions in TC31 WG22 October 2015 TC/SC involved: IEC/TC 31 |
| Question: When an Ex equipment or Ex component is to include an IP rating as part of both the marking and the certificate, what test program is required to support the IP rating? Answer: To answer this question, evaluations involving explosive gas atmospheres must be considered separately from evaluations involving explosive dust atmospheres in accordance with the following… Evaluations involving explosive gas atmospheres It must first be understood that the specific IEC Ex type of protection standards for explosive gas atmospheres do not require marking of an IP rating. Further, neither does the latest 2011 edition of IEC 60079-0. These IEC Ex standards for the various types of protection define minimum levels of enclosure requirements associated with specific IP ratings, with these minimum levels of IP requirements needing to be preceded by the applicable order of tests detailed in IEC 60079-0 (such as thermal conditioning, impact, etc.). Compliance with this minimum level of IP requirements in the applicable IEC Ex standards allows for optional (but not mandatory) inclusion of the associated IP rating as part of both the marking and certificate. Based on the above understanding, after an Ex equipment or Ex component is determined to comply with the applicable minimum level of IP requirements per the applicable IEC Ex type of protection standard(s), the manufacturer may request additional IP testing associated with an IP rating other than that addressed by the requirements in the applicable IEC type of protection standard(s). When a manufacturer makes such a request for additional IP testing, it is outside the requirements of these IEC Ex standards. As such, this additional IP testing need only comply with IEC 60529 or IEC 60034-5 as applicable, and not with any of the testing detailed in IEC 60079-0. Compliance with an IP rating in accordance with only IEC 60529 or IEC 60034-5 as applicable allows for optional (but not mandatory) inclusion of this associated IP rating as part of both the marking and certificate. If the additional IP rating is to be marked on the equipment, it shall not form an integral part of the hazardous area coding required by IEC 60079-0. If the additional IP rating is to be given in the certificate, it shall only be mentioned in the schedule of the certificate, with the explanation that it is in accordance with IEC 60529 or IEC 60034-5 and that (if applicable) the testing was not performed in accordance with the pre-conditioning required by IEC 60079-0. Note: To minimize samples needing to be tested, consideration should be given to simply performing the additional IP testing as part of the test sequence required by the applicable IEC Ex standards. Evaluations involving explosive dust atmospheres Regarding evaluations involving explosive dust atmospheres, depending on the dust standards being applied, the requirements regarding IP testing differ. If IEC 60079-0:2011 is being used, along with IEC 60079 series standards that now incorporate requirements for explosive dust atmospheres, the inclusion of an optional IP rating as part of both the marking and certificate would be in accordance with evaluations involving explosive gas atmospheres as noted above. If IEC 60079-0:2007 or any of the IEC 61241 series is being used for evaluations involving explosive dust atmospheres, there is a requirement for these to include an IP marking. Therefore, the inclusion of an IP rating as part of both the marking and certificate is mandatory. In addition, because an IP rating is mandatory, the IP rating that is part of both the marking and certificate shall be supported by all required testing in the applicable explosive dust standard(s), including any required pre-conditioning, etc. |  |  |