- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Circulated to: ExTAG – IECEx Testing and Assessment Group

TITLE: Draft ExTAG Decision Sheet – Marking of Ex t equipment intended for installation partly in Zone 20 and partly in Zone 21

INTRODUCTION

ExTAG/316/CD was listed for discussion during the ExTAG The Hague 2014 Meeting however due to the lack of time the decision was taken that comment be considered via correspondence.

This document, ExTAG/316A/CD, has been prepared by the ExTAG Chairman, at that time, Mr Ron Sinclair, with IEC/TC31 WG22 / MT 60079-14 involvement, and takes into account comment received since 2014 and circulated in ExTAG/334A/CC . Changes included in this updated draft are shown in red text.

This updated draft document is issued for consideration during the upcoming ExTAG Christchurch Meeting.

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

COLLECTION OF IECEx / ExTAG DECISION

| Standard: IEC 60079-31:2008 (Ed. 1.0) IEC 60079-0:2007 (Ed. 5.0) IEC 60079-0:2011 (Ed. 6.0) | Clause: 7 29.4 29.5 |  |
| --- | --- | --- |
| Subject: Marking of Ex t equipment intended for installation partly in Zone 20 and partly in Zone 21 Status of document: Draft | Key words: - Marking - Ex t | - Date: 2015 07 29 Originator of proposal: ExTAG Chairman TC/SC involved: IEC/TC31 WG22 / MT 60079-14 |
| Background: Questions have been raised on how equipment with dust protection by enclosure should be marked when it is intended for partial installation in Zone 20 and partial installation in Zone 21, for example equipment mounted through the wall of a process vessel or silo. A search of existing certificates shows that this has been handled in different ways by different ExCBs. Some certificates exist using the construct for marking “Ex ta/tb” with or without “Da/Db” although this is not foreseen in any of the relevant standards (though presumably adopted from the practice outlined in IEC 60079-26 for gas and vapour protected equipment). The significance of the marking may or may not have been explained in the text of the certificate. IEC 60079-14 makes no reference to assist. Other certificates exist which show separate full codes for the different parts of the equipment. According to the IECEx Certificate database, all the ExCBs that have used the construct Ex ta/tb are also Notified Bodies for the ATEX Directive and it is recognised that it would be acceptable to use Ex ta/tb Category 1D/2D for ATEX. However, for IECEx there is a requirement of strict conformity to the standards. Question: How is marking of equipment to be handled when equipment with dust protection by enclosure is intended to have two levels of protection, for mounting, for example, in a boundary wall between Zone 20 and Zone 21? Draft Answer: It is a point of principle that IECEx Certification is based on strict conformity with the relevant standards. Accordingly, such equipment should be provided with two separate marking strings, with the application of the marking clearly explained in both the certificate and the instruction, and the specific conditions of use relating to this installation should be indicated by appending an ‘X’ to the certificate number in accordance with 29.3 e) of IEC 60079-0. If the marking construct “Ex ta/tb Da/Db” is to be used, this will require an amendment to the published standards. |  |  |