INTERNATIONAL ELECTROTECHNICAL COMMISSION SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE

IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Circulated to: ExTAG – IECEx Testing and Assessment Group

TITLE:  Draft ExTAG Decision Sheet – Temperature measurement of cable entries on electrical machines

INTRODUCTION

This updated ExTAG Draft Decision Sheet ExTAG/276A/CD ExTAG Draft Decision Sheet – Temperature measurement of cable entries on electrical machines has been prepared taking into account comment received, on ExTAG/276/CD.

It is now issued for a 4 week comment period.

Please submit comments using the attached Comments Table by-

Comment to forwarded by 2013 01 15 to

Christine Kane

If no comments are received the document will proceed for publication.

On behalf of Mr. Brenon

- Michel Brenon

ExTAG Secretary

| Address: IECEx Secretariat 286 Sussex Street Sydney NSW 2000 Australia | Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 E-mail: chris.agius@iecex.com http://www.iecex.com | ExTAG Secretary Mr Michel Brenon/LCIE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 e-mail michel.brenon@lcie.fr |
| --- | --- | --- |

| Member Body/ Country | Clause/ Sub-clause | Paragraph Figure/ Table | Type of comment General/ technical/ editorial | COMMENTS | Proposed change | Observation |
| --- | --- | --- | --- | --- | --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-0:2011 IEC 60079-0:2007 | Clauses: 16.6 16.5 |  |
| --- | --- | --- |
| Subject: Temperature measurement of cable entries on electrical machines Status of document: Draft | Key words: - Cable entries - Branching point - Temperature measurement | # Date: Originator of proposal: IEC TC31 WG27 via Chairman ExTAG TC/SC involved: IEC/TC 31 |
| Question: Clause 16.6 of IEC 60079-0:2011 states “When the temperature under rated conditions is higher than 70 °C at the entry point or 80 °C at the branching point of the conductors, information shall be marked on the equipment exterior to provide guidance to the user on the proper selection of cable and cable gland or conductors in conduit.” It is not normal practice for electrical machines to be tested with the cable entry devices and cables that might be used in an actual installation, but with the cables available at the manufacturer’s test area. In many cases, there will be no formal entry device as the cables will enter via the space reserved for fixing of a gland plate. How shall the relevant entry point and branching point temperatures be determined? Answer: This subject was discussed at the TC31 WG27 meeting in Oslo in September 2012. WG27 resolved that a note should be added to IEC 60079-0 to clarify the testing requirement. Until such a note is added, WG27 requested that the following clarification be issued as an ExTAG Decision Sheet: The use of the internal air space temperature to represent the service temperature of terminal box gaskets and seals, the cable branching point temperature, and the entry point temperature reflects the normal practice of testing machines without prior knowledge of the actual glands and cables to be used for installation. The production of heat from the machine connections is generally insignificant with respect to the production of heat from the machine windings and core. Further amplification: - The entry point of the cable where the temperature is measured should be sealed so far as possible to ensure that there is minimum air-circulation which can reduce the measured temperature. - This is not intended to apply to any gasket between the terminal box and the frame of the machine, where higher temperatures may be recorded, but only to the gasket between the terminal box and its lid. - Although written in the context of electrical machines, there may be other types of equipment where an equivalent approach is applicable |  |  |