INTERNATIONAL ELECTROTECHNICAL COMMISSION SYSTEM FOR CERTIFICATION

TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Title: NOTICE TO ExTLS and ExCBs - New Edition of IEC 60079-0 and ExTAG

- DS 2010/006A

Circulated to: Ex Testing and Assessment Group (ExTAG)

The IECEx 02 Rules have a clear requirement that a new IECEx Certificate of Conformity can only be issued to the current edition or 1 edition prior of a Standard, of course with the exception that this rule does not apply when issuing IECEx Unit Verification Certificates.

- The fact that IEC protection Technique Standards have included dated references to the General Requirements Standard IEC 60079-0, ExTAG produced Decision Sheet DS 2010/006 to assist in clarifying the approach as we see IEC 60079-0 revised and newer editions being issued.  This Decision Sheet was further revised as ExTAG DS 2010/006A, as agreed during the Berlin 2010 meeting.

- To assist in situations where applications for ExTRs and or CoCs were made well prior to the new DS 2010/006A, (projects in hand with ExTLs and ExCBs) the IECEx Executive have determined that the edition of IEC 60079-0 that is referenced by the Ex protection Technique Standard may be used and shown on the IECEx Certificate of Conformity.

- For example, while the 5th edition of IEC 60079-11 may be used for the purposes of issuing a new CoC, IEC 60079-11 5th Edition refers to requirements of IEC 60079-0 4th Edition.  Despite the fact that IEC 60079-0 6th Edition has recently been published, IEC 60079-0 4th edition maybe used in this situation BUT only for projects where applications were made prior to introduction of DS 2010/006A.

- This will enable ExTLs and ExCBs to finalise existing projects while preparing for the implementation of DS 2010/006A.

| Address: SAI Global Building 286 Sussex Street Sydney NSW 2000 Australia | IECEx Secretariat Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 e-mail: chris.agius@iecex.com http://www.iecex.com | ExTAG Secretary Mr Michel Brenon/LCIE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 e-mail michel.brenon@lcie.fr |
| --- | --- | --- |

Therefore, in summary the following applies

- All ExCBs and ExTLs must be aware and be implementing Revised Decision Sheet, DS 2010/006A, as well of course with all ExTAG Decision Sheets as listed at http://www.iecex.com/extag_decisions.htm

- For projects currently in hand within ExTLs and ExCBs, where the application was made prior to introduction of DS 2010/006A, these may continue and issue new IECEx Certificates of Conformity showing compliance with IEC 60079-0 4th Edition, where the Ex protection technique Standard complies with the requirements of IECEx 02 being either the current edition or 1 edition prior

- The exemption granted under item 2 above applies only where projects are in hand and the application was made prior to issue of the new DS 2010/006A.  The IECEx Executive expect that such projects would be at a mature stage and should be finalised within not more than 3 months.

To assist, attached is a copy of the DS 2010/006A as referred to in this notice

Chris Agius

IECEx Executive Secretary

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-1, -2, -5, -6, -7, -11, -15 and -18 | Clauses: Normative references to IEC 60079-0 |  |
| --- | --- | --- |
| Subject: Dated references to IEC 60079-0 from specific type of protection standards within the IEC 60079 series Status of document: Approved | Key words: - Normative references - General requirements - Dated references | # Date: 110629 Originator of proposal: ETL/FMG/UL TC/SC involved: IEC/TC31 and IEC/SC31G |
| Background: - While the current intent within IEC/TC 31 is to remove dated references to IEC 60079-0 from the IEC 60079 series type of protection standards, many specific parts have not yet had a chance to fully process this intent. - It will be several years before all the necessary revisions can be published to remove these dated references due to defined maintenance cycles. - The dated references that still exist in many of the IEC 60079 series type of protection standards are to IEC 60079-0:2004 (Ed. 4), even though the latest edition of the general requirements standard is IEC 60079-0:2011 (Ed. 6). - The only protection techniques with undated references today are the current editions of -6, -11, -15, and -18. - This complicates IECEx evaluations under the following scenarios, noting that IECEx permits Certificates of Conformity to be issued only against the current or one prior edition;… - The manufacturer is specifically requesting certification to IEC 60079-0:2007 (Ed. 5) or IEC 60079-0:2011 (Ed. 6) and the standards for the types of protection reference IEC 60079-0:2004 (Ed. 4) which is no longer a permitted IECEx Certification standard or - The manufacturer is requesting certification to IEC 60079 series standards that involve multiple protection techniques in which these multiple protection techniques include both undated references, and dated references to IEC 60079-0:2004 (Ed. 4) which is no longer a permitted IECEx Certification standard. Note: The significant differences between IEC 60079-0:2004 (Ed. 4) and IEC 60079-0:2007 (Ed. 5) are as follows... - Requirements for explosive dust atmospheres transferred from IEC 61241-0. - The marking Group “II” alone has been replaced by “IIA”, “IIB”, or “IIC” as many of the enclosure requirements are now aligned with a specific sub-group. - Dust groups defined as Group IIIA, IIIB and IIIC. - Limits for ultrasonic and electromagnetic radiation introduced. - Remainder of “electrostatic” requirements transferred from IEC 60079-26. - Equipment protection levels (EPL) introduced. - Transition of term from “apparatus” to “equipment” (where appropriate). Note: The significant differences between IEC 60079-0:2007 (Ed. 5) and IEC 60079-0:2011 (Ed. 6) are as follows... - Expansion of material specification data for plastics and elastomers, including UV resistance - Addition of alternative qualification for O-rings - Addition of alternative criteria for surface resistance - Addition of breakdown voltage limit for non-metallic layers applied to metallic enclosures - Expansion of “X” marking options for non-metallic enclosure materials not meeting basic electrostatic requirements - Clarification that non-metallic enclosure requirements also apply to painted or coated metal enclosures - Clarification of test to determine capacitance of accessible metal parts with reduction in acceptable capacitance - Addition of limits on zirconium content for Group III and Group II (Gb only) enclosures - Introduction of “X” marking for Group III enclosures not complying with basic material requirements, similar to that existing for Group II - Addition of button-head cap screws to permitted “Special Fasteners” - Reference for protective earthing (PE) requirements for electrical machines to IEC 60034 1 - Addition of requirements for ventilating fans - Addition of alternative construction for disconnectors - Removal of voltage limits on plugs and sockets - Addition of test requirements for arc-quenching test on plugs and sockets - Revision to impact test of glass parts - Revision to impact test procedure to address “bounce” of impact head - Clarification of the test requirements for “service” and “surface” temperature - Addition of temperature rise tests for converter-fed motors - Addition of alternative test method for thermal endurance - Removal of “charging test” and addition of note providing guidance - Clarification of test for the measurement of capacitance - Addition of a “Schedule of Limitations” to certificates for Ex Components - Clarification of the marking for multiple temperature classes - Addition of marking for converter-fed motors - Removal of IP marking for Group III - Addition of specific instructions for electrical machines - Addition of specific instructions for ventilating fans Question: In agreement with the manufacturer, can IECEx ExCBs issue IECEx ExTRs and CoCs that, for the IEC 60079-0 general requirements, only involve either the 2007 edition (Ed. 5) or 2011 edition (Ed. 6), even if the involved specific protection technique part(s) reference the 2004 edition (Ed. 4)? Answer: Yes, under the following procedure: - All requirements in either IEC 60079-0:2007 (Ed. 5) or IEC 60079-0:2011 (Ed. 6), as applicable, shall be applied and detailed in an ExTR for IEC 60079-0:2007 (Ed. 5) or IEC 60079-0:2011 (Ed. 6), as applicable. - Reference to IEC 60079-0:2007 (Ed. 5) or IEC 60079-0:2011 (Ed. 6) shall be indicated in the CoC and ExTR under the respective "Standards" sections. - The Cover page of the ExTR shall include a brief statement under the “General Remarks” section that reads: “IEC 60079-0:2007 (Ed. 5) [or IEC 60079-0:2011 (Ed. 6)] was used for the general requirements at the request of the manufacturer in accordance with DS 2010/006, even though the involved IEC 60079 series protection technique standard(s) may reference IEC 60079-0:2004 (Ed. 4)”, or equivalent. This comment is to be included to help avoid any potential confusion on the part of a Receiving ExCB. As the standards for “i” and “n” have more complicated references to IEC 60079-0, shown in a Table in Clause 1 of each standard, the following two reference Tables have been included to provide guidance in the application of IEC 60079-0:2007(Ed. 5) or IEC 60079-0:2011 (Ed. 6) with IEC 60079-11:2006 (Ed. 5) and IEC 60079-15:2005 (Ed. 3), both of which include extensive edition-specific references to IEC 60079-0:2004(Ed. 4). The additional references to Edition 5 and Edition 6 are shown in the “grey” columns at the left of each Table. |  |  |

IEC 60079-11:2006 (Ed. 5)

Table 1 – Exclusion of specific clauses of IEC 60079-0

| Clause or subclause of IEC 60079-0 |  |  |  | Intrinsically safe apparatus | Associated apparatus |
| --- | --- | --- | --- | --- | --- |
| 2011 (Ed. 6) | 2007 (Ed. 5) | 2004 (Ed. 4) |  |  |  |
| 29.4.d | 29.3.d | 4.2.2 | Group II – Surface temperature marking | Applies | Excluded |
| 5.3 | 5.3 | 5.3 | Maximum surface temperature | Applies | Excluded |
| 5.3.2.2 | 5.3.2.2 | 5.4 | Surface temperature and ignition temperature | Applies | Excluded |
| 5.3.3 | 5.3.3 | 5.5 | Small components | Applies | Excluded |
| 6.3 | 6.3 | 6.3 | Opening times | Excluded | Excluded |
| 7.1.1 | 7.1.1 | 7.1.1 | Applicability | Applies | Excluded |
| 7.1.2 | 7.1.2 | 7.1.2 | Specification of materials | Applies | Excluded |
| 7.1.2* | 7.1.3* | 7.1.3* | Plastic materials | Excluded | Excluded |
| 7.2* | 7.2* | 7.2* | Thermal endurance | Excluded | Excluded |
| 7.4 | 7.4 | 7.3 | Electrostatic charges on external non-metallic materials of enclosures | Applies | Excluded |
| 7.4.2 | 7.4.2 | 7.3.2 | Avoidance of a build-up electrostatic charge | Applies | Excluded |
| 7.5 | 7.5 | 7.4 | Threaded holes | Excluded | Excluded |
| 8.1 | 8.1 | 8.1 | Material composition | Applies | Excluded |
| 8.2 | 8.2 | 8.2 | Threaded holes | Excluded | Excluded |
| 9 | 9 | 9 | Fasteners | Excluded | Excluded |
| 10 | 10 | 10 | Interlocking devices | Excluded | Excluded |
| 11 | 11 | 11 | Bushings | Excluded | Excluded |
| 12 | 12 | 12 | Materials used for cementing | Excluded | Excluded |
| 14 | 14 | 14 | Connection facilities and terminal compartments | Excluded | Excluded |
| 15 | 15 | 15 | Connection facilities for earthing or bonding conductors | Excluded | Excluded |
| 16.5 | 16.5 | 16.5 | Conductor temperature | Excluded | Excluded |
| 17 | 17 | 17 | Supplementary requirements for rotating electrical machines | Excluded | Excluded |
| 18 | 18 | 18 | Supplementary requirements for switchgear | Excluded | Excluded |
| 19 | 19 | 19 | Supplementary requirements for fuses | Excluded | Excluded |
| 20 | 20 | 20 | Supplementary requirements for plugs and sockets | Excluded | Excluded |
| 21 | 21 | 21 | Supplementary requirements for luminaires | Excluded | Excluded |
| 22 | 22 | 22 | Supplementary requirements for caplights and handlights | Excluded | Excluded |
| 23.2 | 23.2 | 23.1 | Batteries | Applies | Excluded |
| 26.4 | 26.4 | 26.4 | Tests of enclosures | Applies | Excluded |
| 26.5.1 | 26.5.1 | 26.5.1 | Temperature measurement | Applies | Excluded |
| 26.5.2 | 26.5.2 | 26.5.2 | Thermal shock test | Excluded | Excluded |
| 26.5.3 | 26.5.3 | 26.5.3 | Small component ignition test | Applies | Excluded |
| 26.6 | 26.6 | 26.6 | Torque test for bushings | Excluded | Excluded |
| 26.7* | 26.7* | 26.7* | Non-metallic enclosures or non-metallic parts of enclosures | Excluded | Excluded |
| 26.8* | 26.8* | 26.8* | Thermal endurance to heat | Excluded | Excluded |
| 26.9* | 26.9* | 26.9* | Thermal endurance to cold | Excluded | Excluded |
| 26.10* | 26.10* | 26.10* | Resistance to light | Excluded | Excluded |
| 26.11* | 26.11* | 26.11* | Resistance to chemical agents for Group I electrical apparatus | Excluded | Excluded |
| 26.12 | 26.12 | 26.12 | Earth continuity | Excluded | Excluded |
| 26.13 | 26.13 | 26.13 | Surface resistance test of parts of enclosures or non-metallic materials | Applies | Excluded |
| NR | 26.14 | 26.14 | Charging tests | Applies | Excluded |
| 26.14 | 26.15 | 26.15 | Measurement of capacitance | Applies | Excluded |
| Annex A | Annex A | Annex A | Ex cable glands | Excluded | Excluded |
| * indicates that these requirements apply for 6.1.2a) only. Applies – This requirement of IEC 60079-0 is applied without change. Excluded – This requirement of IEC 60079-0 does not apply. NR – No requirements. |  |  |  |  |  |

IEC 60079-15:2005 (Ed. 3)

Table 1 – Exclusion of specific clauses of IEC 60079-0

| Clause of IEC 60079-0 |  |  |  | IEC 60079-0 clause application to IEC 60079-15 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2011 (Ed. 6) | 2007 (Ed. 5) | 2004 (Ed. 4) |  | Type of protection1 nC | Non sparking apparatus nA and nA nL | Restricted breathing apparatus nR | Energy limited apparatus nL | Associated energy limited apparatus [nL] and [Ex nL] |
| 4 | 4 | 4 | Apparatus grouping and temperature classification | Yes | Yes | Yes | Yes | Yes |
| 5 | 5 | 5 | Temperatures |  |  |  |  |  |
| 5.1 | 5.1 | 5.1 | Environmental influences | Yes | Yes | Yes | Yes | Yes |
| 5.2 | 5.2 | 5.2 | Service temperature | Yes | Yes | Yes | Yes | Yes |
| 5.3 | 5.3 | 5.3 | Maximum surface temperature | Yes | Yes | Yes | Yes | No |
| 5.3.2.2 | 5.3.2.2 | 5.4 | Surface temperature and ignition temperature | No | No | No | No | No |
| 5.3.3 | 5.3.3 | 5.5 | Small components | Yes | Yes | Yes | Yes | No |
| 6 | 6 | 6 | Requirements for all electrical apparatus |  |  |  |  |  |
| 6.1 | 6.1 | 6.1 | General | Yes | Yes | Yes | Yes | Yes |
| 6.2 | 6.2 | 6.2 | Mechanical strength of apparatus | Yes | Yes | Yes | Yes See Note 3 | No |
| 6.3 | 6.3 | 6.3 | Opening times | No | No | Yes | No | No |
| 6.4 | 6.4 | 6.4 | Circulating currents | Yes | Yes | Yes | No | No |
| 6.5 | 6.5 | 6.5 | Gasket retention | Yes | Yes | Yes | Yes | No |
| 7 | 7 | 7 | Non-metallic enclosures and non-metallic parts of enclosures |  |  |  |  |  |
| 7.1 | 7.1 | 7.1 | General | Yes | Yes | Yes | Yes | No |
| 7.2 | 7.2 | 7.2 | Thermal endurance | Yes | Yes | Yes | Yes | No |
| 7.4 | 7.4 | 7.3 | Electrostatic charges on external non-metallic materials of enclosures | Yes | Yes | Yes | Yes | No |
| 7.5 | 7.5 | 7.4 | Threaded holes | Yes | Yes | Yes | Yes | No |
| 8 | 8 | 8 | Enclosures containing light metals |  |  |  |  |  |
| 8.1 | 8.1 | 8.1 | Material composition | Yes | Yes | Yes | Yes | No |
| 8.2 | 8.2 | 8.2 | Threaded holes | Yes | Yes | Yes | Yes | No |
| 9 | 9 | 9 | Fasteners |  |  |  |  |  |
| 9.1 | 9.1 | 9.1 | General | Yes | Yes | Yes | Yes | No |
| 9.2 | 9.2 | 9.2 | Special fasteners | No | No | No | No | No |
| 9.3 | 9.3 | 9.3 | Holes for special fasteners | No | No | No | No | No |
| 10 | 10 | 10 | Interlocking devices | No | No | No | No | No |
| 11 | 11 | 11 | Bushings | Yes | Yes | Yes | Yes | No |
| 12 | 12 | 12 | Materials used for cementing | No | No | No | No | No |
| 13 | 13 | 13 | Ex components | No | No | No | No | No |
| 14 | 14 | 14 | Connection facilities and terminal compartments | No | No | No | No | No |
| 15 | 15 | 15 | Connection facilities for earthing or bonding conductors | Yes | Yes | Yes | Yes | No |
| 16 | 16 | 16 | Entries into enclosures | Yes | Yes | Yes | Yes | No |
| 17 | 17 | 17 | Supplementary requirements for rotating electrical machines | No | Yes | No | No | No |
| 18 | 18 | 18 | Supplementary requirements for switchgear | Yes | Yes | Yes | No | No |
| 19 | 19 | 19 | Supplementary requirements for fuses | No | No | No | No | No |
| 20 | 20 | 20 | Supplementary requirements for plugs and sockets | No | No | No | No | No |
| 21 | 21 | 21 | Supplementary requirements for luminaires | No | No | No | No | No |
| 23 | 23 | 23 | Apparatus incorporating cells and batteries | Yes | Yes | Yes | Yes | No |
| 24 | 24 | 24 | Documentation | Yes | Yes | Yes | Yes | Yes |
| 25 | 25 | 25 | Compliance of prototype or sample with documents | Yes | Yes | Yes | Yes | Yes |
| 26 | 26 | 26 | Type tests |  |  |  |  |  |
| 26.1 | 26.1 | 26.1 | General | Yes | Yes | Yes | Yes | Yes |
| 26.2 | 26.2 | 26.2 | Test configuration | Yes | Yes | Yes | Yes | Yes |
| 26.3 | 26.3 | 26.3 | Tests in explosive test mixtures | Yes | Yes | Yes | Yes | Yes |
| 26.4 | 26.4 | 26.4 | Tests of enclosures |  |  |  |  |  |
| 26.4.1 | 26.4.1 | 26.4.1 | Order of tests | No | No | No | No | No |
| 26.4.2 | 26.4.2 | 26.4.2 | Resistance to impact | Yes | Yes | Yes | Yes | No |
| 26.4.3 | 26.4.3 | 26.4.3 | Drop test | Yes | Yes | Yes | Yes | No |
| 26.4.4 | 26.4.4 | 26.4.4 | Acceptance criteria for test for resistance to impact and drop test | Yes | Yes | Yes | Yes | No |
| 26.4.5 | 26.4.5 | 26.4.5 | Degree of protection IP by enclosures | No | No | No | No | No |
| 26.5 | 26.5 | 26.5 | Thermal tests |  |  |  |  |  |
| 26.5.1 | 26.5.1 | 26.5.1 | Temperature measurement | Yes | Yes | Yes | Yes | No |
| 26.5.2 | 26.5.2 | 26.5.2 | Thermal shock test | Yes | Yes | Yes | Yes | No |
| 26.5.3 | 26.5.3 | 26.5.3 | Small component ignition test | Yes | Yes | No | Yes | No |
| 26.6 | 26.6 | 26.6 | Torque test for bushings | Yes | Yes | Yes | Yes | Yes |
| 26.6.1 | 26.6.1 | 26.6.1 | Procedure | Yes | Yes | Yes | Yes | Yes |
| 26.6.2 | 26.6.2 | 26.6.2 | Acceptance criteria | Yes | Yes | Yes | Yes | Yes |
| 26.7 | 26.7 | 26.7 | Non-metallic enclosures or of non-metallic parts of enclosures |  |  |  |  |  |
| 26.7.1 | 26.7.1 | 26.7.1 | General | Yes | Yes | Yes | Yes | No |
| 26.7.2 | 26.7.2 | 26.7.2 | Temperatures during tests | Yes | Yes | Yes | Yes | No |
| 26.8 | 26.8 | 26.8 | Thermal endurance to heat | Yes | Yes | Yes | Yes | No |
| 26.9 | 26.9 | 26.9 | Thermal endurance to cold | Yes | Yes | Yes | Yes | No |
| 26.10 | 26.10 | 26.10 | Resistance to light | Yes | Yes | Yes | Yes | No |
| 26.11 | 26.11 | 26.11 | Resistance to chemical agents for Group I electrical apparatus | No | No | No | No | No |
| 26.12 | 26.12 | 26.12 | Earth continuity | Yes | Yes | Yes | Yes | No |
| 26.13 | 26.13 | 26.13 | Surface resistance test of parts of enclosures of non-metallic materials | Yes | Yes | Yes | Yes | No |
| NR | 26.14 | 26.14 | Charging tests to verify the inability to store a dangerous charge | Yes | Yes | Yes | Yes | No |
| 26.14 | 26.15 | 26.15 | Measurement of capacitance to verify the inability to store a dangerous charge | Yes | Yes | Yes | Yes | No |
| 26.14.1 | 26.15.1 | 26.15.1 | Procedure | Yes | Yes | Yes | Yes | No |
| 26.14.2 | 26.15.2 | 26.15.2 | Acceptance criteria | Yes | Yes | Yes | Yes | No |
| 27 | 27 | 27 | Routine verifications and tests | Yes | Yes | Yes | Yes | Yes |
| 28 | 28 | 28 | Manufacturer's responsibility | Yes | Yes | Yes | Yes | Yes |
| 28.2 | 28.2 | 28.1 | Certificate | Yes | Yes | Yes | Yes | Yes |
| 28.3 | 28.3 | 28.2 | Responsibility for marking | Yes | Yes | Yes | Yes | Yes |
| 29 | 29 | 29 | Marking | Yes | Yes | Yes | Yes | Yes |
| 30 | 30 | 30 | Instructions | Yes | Yes | Yes | Yes | Yes |
| NOTE 1 An entry of “Yes” in the table indicates the requirements of the referenced section of IEC60079-0 apply. An entry of “No” indicates the requirements either do not apply or have been modified by IEC 60079-15. NOTE 2 Type of protection nC includes encapsulated devices, enclosed break devices, non-incendive components, sealed devices, and hermetically sealed devices. NOTE 3 Clause 6.2 is a calling clause for the tests in 26.4 which are different for both portable and fixed apparatus. |  |  |  |  |  |  |  |  |