INTERNATIONAL ELECTROTECHNICAL COMMISSION SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE

IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Circulated to: ExTAG – IECEx Testing and Assessment Group

TITLE: Draft Decision Sheet - A decision is required from the IECEx to confirm or negate the locked rotor test as a mandatory requirement in IEC 60079-19.

INTRODUCTION

This updated draft has been prepared as a result of discussions held during the 2011 ExTAG Split meeting and of comment received on ExTAG/196B/CD.  It is now issued for a 4 week comment period.

Please note the highlighted area contains additional or altered text.

Please submit comments using the attached Comments Table by-

Comment to forwarded by 2012 03 12 to

Christine Kane

On behalf of Mr. Brenon

## Michel Brenon

ExTAG Secretary

| Address: IECEx Secretariat 286 Sussex Street Sydney NSW 2000 Australia | Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 E-mail: chris.agius@iecex.com http://www.iecex.com | ExTAG Secretary Mr Michel Brenon/LCIE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 e-mail michel.brenon@lcie.fr |
| --- | --- | --- |

| Member Body/ Country | Clause/ Sub-clause | Paragraph Figure/ Table | Type of comment General/ technical/ editorial | COMMENTS | Proposed change | Observation |
| --- | --- | --- | --- | --- | --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: Standard IEC60079-19:2006 | Clauses: 5.2.6.3.2, 7.2.6.3.2, 8.2.6.3.2, 9.2.6.3.2 & 11.2.5.2.2 |  |
| --- | --- | --- |
| Subject: Locked rotor test for rewound rotating machines Status of document: Draft | Key words: Locked rotor test | # Date: Revised July 2011 Originator of proposal: GB |
| Question: Is it obligatory to conduct the locked rotor test given as item b) in the following clauses of IEC 60079-19:2006 5.2.6.3.2 7.2.6.3.2 8.2.6.3.2 9.2.6.3.2 11.2.5.2.2 Answer: No The equivalent clause in the latest version of this standard (IEC 60079-19:2010) shall be used for interpretation of these clauses. e.g.: 5.2.6.3.2.b b) The stator windings of cage machines shall be energized at an appropriate reduced voltage, with the rotor locked, to obtain between 75 % and 125 % of full-load current and to check balance on all phases. (The test, which in some respects is an alternative to a full-load test, is used to confirm the integrity of the stator winding and its connections and to indicate the presence of rotor defects.) Unbalance shall be less than 5 % of middle value. NOTE 2 Where this test is not reasonably practical other means of verification should be used. Clause Number IEC 60079-19:2006 Equivalent Clause Number IEC 60079-19:2010 5.2.6.3.2.b 5.2.6.3.2.b 7.2.6.3.2.b 7.2.6.3.2.b 8.2.6.3.2.b 8.2.6.3.2.b 2nd Para 9.2.6.3.2.b 9.2.6.3.2.b 11.2.5.2.2.b 11.2.6.3.2.b The alternative tests need to verify the integrity of the rotor winding , the polarity of all coils in a phase and the integrity of stator connections Other tests could include, but not limited to, NDT tests of rotor bar connections, proprietary rotor winding test equipment, stator bearing test, thermographic verification of stator winding connections with current etc |  |  |