INTERNATIONAL ELECTROTECHNICAL COMMISSION SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE

IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Circulated to: ExTAG – IECEx Testing and Assessment Group

TITLE: Draft decision Sheet - Voltage values in determination of creepage and clearance distances

INTRODUCTION

This proposed draft ExTAG Decision Sheet was prepared by UL, US, and is issued for your consideration.

Please submit comments by -

30th November 2009 to ExTAG Secretary, Mr. Michel Brenon, via

Christine Kane

If comments have not been received by the above date this document will be published as an ExTAG Decision Sheet.

## Michel Brenon

ExTAG Secretary

| Address: IECEx Secretariat 286 Sussex Street Sydney NSW 2000 Australia | Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 E-mail: chris.agius@iecex.com http://www.iecex.com | ExTAG Secretary Mr Michel Brenon/LCIE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 e-mail michel.brenon@lcie.fr |
| --- | --- | --- |

| Member Body | Clause/ Subclause | Paragraph Figure/ Table | Type of comment General/technical/ editorial | COMMENTS | Proposed change | Observation |
| --- | --- | --- | --- | --- | --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-7:2001 IEC 60079-7:2006 | Clause: Table 1 |  |
| --- | --- | --- |
| Subject: Voltage values in determination of creepage and clearance distances Status of document: | Key words: - Creepage and Clearance Distances - Working Voltage | # Decision of members: # Date: Originator of proposal: J.Dinneen/UL TC/SC involved: |
| Question: When determining the creepage and clearance distances from the voltage in Table 1, if the working voltage is between two voltage values described in the table, would the next higher voltage be applied? Background: In IEC 60079-7:1990, and other IEC standards (e.g. IEC 60079-15) it is clear that the user of the standard shall apply the next highest voltage level based on the less than/equal to symbol (<) next to the voltage values. In IEC 60079-7: 2001 and 2006, the less than/equal to symbols are not included in Table 1, so it is not clear whether the next higher voltage shall be applied. This could imply that extrapolation between the listed values is permitted. For example: Voltage Minimum Clearance required by 60079-7 - 4,0 250 5,0 If the voltage in question is, for example, 225 V, is the required spacing 5,0 mm, or can it be extrapolated to 4,5 mm? Answer: If the working voltage is between two voltage values described in Table 1, the value for the higher voltage level shall be applied when determining the creepage and clearance distances, unless the working voltage is within  10% of voltage values in accordance with Note 1. In the example above, the required spacing is 5,0 mm. |  |  |
| Final wording might be changed when creating CDV and FDIS document versions. |  |  |