### INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

Title: Draft Decision Sheet – Sealing requirements and terminology of cable glands

Circulation: ExTAG Members

##### INTRODUCTION

This Draft Decision Sheet, prepared by SP Technical Research Institute of Sweden, is issued for your consideration.

Please submit comments by -

21st August 2009 to ExTAG Secretary, Mr. Michel Brenon, via Christine Kane

Should comments be received on this Draft Decision Sheet they will be discussed during the ExTAG Melbourne Meeting to be held 1st September 2009

Michel Brenon

ExTAG Secretary

| Address: SAI Global Building 286 Sussex Street Sydney NSW 2000 Australia | IECEx Secretariat Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 e-mail: chris.agius@iecex.com http://www.iecex.com | ExTAG Secretary Mr Michel Brenon/LCIE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 e-mail michel.brenon@lcie.fr |
| --- | --- | --- |

| Member Body | Clause/ Subclause | Paragraph Figure/ Table | Type of comment General/technical/ editorial | COMMENTS | Proposed change | Observation |
| --- | --- | --- | --- | --- | --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-31:2008 (Ed 1) | Clauses: 5.1.2, 5.2.1 |  |
| --- | --- | --- |
| Subject: Sealing requirements and terminology of cable glands Status of document: Draft | Key words: - Cable gland - Cable gland sealing - Terminology for cable glands | # Date: 090709 Originator of proposal: SP TC/SC involved: |
| Background (for information – to be removed when issued) This proposed Decision Sheet relates primarily to a type of cable gland intended for one or more cables, with a seal made up of a number of separate elastomeric modules, which are compressed together when the gland is mounted as intended. This type of certified glands have been on the market since many years and the changes in the standard are not believed to preclude continuous use of such glands. Picture Example of a cable gland, with a metal frame with six threaded studs, six elastomeric sealing modules for up to five cables and a compression unit (on the top). Question 1 - sub-clause 5.1.2 in IEC 60079-31:2008 Sub-clause 5.1.2 requires seals in enclosure joints to be of “one-piece continuous construction”. Does this sub-clause apply for internal seals of cable glands (seals between the frame of a cable gland and the cables)? Answer No. Considering that the sub-clause applies for gaskets in joints and considering the definition of joints according to 3.2, this sub-clause is not applicable for internal seals of cable glands. The frame of the gland and the cable, between which the seal is located, is not “two parts of an enclosure” or “the conjunction of enclosures” as stated in the definition. Question 2 - sub-clause 5.2.1 in IEC 60079-31:2008 a) Can cable glands with circular or non-circular form or flanges (including a flange gasket), intended to be mounted on enclosures by threaded fasteners such as threaded studs, bolts and nuts (incl. threaded glands for non-threaded entry holes to be locked by a counter nut), be evaluated as equipment? b) Can cable glands with frames intended to be welded, casted or cemented on an enclosure on field, or cable glands according to a) above but without flange gaskets, be evaluated as equipment? Answer a) Yes, provided that the gland includes flange gasket and the manufacturer’s instructions state that the gland shall be mounted in such a way that the joints between the flange and the enclosure fulfils the required degree of ingress protection after mounting (IP 6X or IP 5X according to 6.1.1). The gland shall be “X”-marked and this condition regarding ingress protection (IP) after mounting, shall be stated on the certificate. b) No. To fasten a gland to an enclosure on field, by welding, casting or cementing, may influence the type of protection “t” related to e.g. temperature and resistance to impact requirements in the standards. Glands according to a) - but without frame sealing – may also influence the type of protection “t”, related to e.g. degree of ingress protection IP. Therefore, such glands shall be evaluated as Ex components, to allow the relevant requirements and tests according to the standards to be applied after the gland has been mounted as intended on an enclosure, to form a complete equipment. |  |  |