### INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SCHEME

FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SCHEME)

Title: ExTAG Draft Decision Sheet 	Assessment and testing of routine dielectric strength test IEC 60079-18:2004

Circulation: ExTAG Members

INTRODUCTION

This proposed draft ExTAG Decision Sheet was prepared by FM Approvals LLC and is issued for your consideration.

Please submit comments by -

26th November 2008 to ExTAG Secretary, Mr. Michel Brenon, via

Christine Kane

If comments have not been received by the above date this document will be published as an ExTAG Decision Sheet.

Michel Brenon

ExTAG Secretary

| Address: SAI Global Building Level 7 286 Sussex Street Sydney NSW 2000 Australia | IECEx Secretariat Contact Details: Tel: +61 2 8206 6940 Fax: +61 2 8206 6272 e-mail: chris.agius@iecex.com http://www.iecex.com | ExTAG Secretary Mr Michel Brenon/LCIE Tel: +33 1 40 95 5519 Fax: +33 1 40 95 5520 e-mail: michel.brenon@lcie.fr |
| --- | --- | --- |

October 2008

- COLLECTION OF IECEx / ExTAG DECISIONS

| - Standard: - lEC 60079-18:2004 | - Clause: - 9.2 | - Sheet No. |
| --- | --- | --- |
| - Subject: - Assessment and testing of routine dielectric strength test - Status: Draft | - Key words: - Dielectric strength - Isolation | ### Decision Sheet Date: 2008-10-17 Originator of proposal: FM Approvals LLC |
| - Related document: |  |  |
| Background (for information only – to be removed when issued): The routine dielectric strength test for an encapsulated assembly is not possible on equipment with EMC protective circuitry connected between the internal circuit and the enclosure since the EMC protection components cannot be disconnected for the test. In this case, the routine dielectric test should not be necessary if the circuit is supplied from a galvanically isolated supply since a failure of the basic insulation would not result in a potentially hazardous condition. Therefore, the intent of the routine dielectric strength test is for circuits that may potentially cause a hazardous condition by use with a non-isolated supply. Question. How can a routine dielectric strength test in an encapsulated assembly with EMC protective circuitry connected between the internal circuit and the enclosure be conducted without disconnection of the EMC protection components? Answer. In the case where, the circuit is supplied from (or required to be supplied from) a galvanically isolated supply, a failure of the basic insulation would not result in a potentially hazardous condition. The routine dielectric test of 9.2 is not required in this case. The symbol “X” shall be placed after the certificate reference, and the “Specific Conditions of Use” shall include the requirement that the encapsulated equipment or Ex Component be supplied from a galvanically isolated supply. |  |  |