- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

TITLE: Draft ExTAG Decision Sheet – Cable transit or entry devices according to IEC 60079-0

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

This document, ExTAG/450/CD Draft ExTAG Decision Sheet – Cable transit or entry devices according to IEC 60079-0, has been prepared by Mr. Peter Thurnherr, member of the IECEx Executive,  in consultation with  IEC TC31 (WG22, MT60079-31 and MT60079-14)

It is issued for a six week comment period for consideration by ExTAG Members.

Please submit comments using the comments table, a separate document by -

2017 05 18 to

Christine Kane

If there are no comments received the document will be forwarded for publication.

Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-0, all Ed. | Clauses: Cl. 16 and Annex A |  |
| --- | --- | --- |
| Subject: Cable transit or entry devices according IEC 60079-0 Status of document: Draft | Key words: - Cable transit device - Entry device - Cable gland | # Date: March 2017 Originator of proposal: Mr. Peter Thurnherr, member of the IECEx Executive, in consultation with IEC TC31 (WG22, MT60079-31 and MT60079-14) |

Background:

It was identified in recent TC31 meetings that the requirements in IEC 60079-0 for entry devices such as cable glands are clearly detailed only for typical cable glands, where the constructional and testing requirements are described in Annex A of IEC 60079-0. Devices such as cable transits, having the same function but are not named as cable glands, are available on the market for normal industrial use. Reading IEC 60079-0, Ed 6, could result in the interpretation that such devices need not fulfill the requirements for cable glands, as it is not clear what requirements are to be applied to such devices. IEC 60079-0, Ed 6, says that it applies to cable transits, but includes no specific requirements. To avoid the certification of cable transits for hazardous areas without fulfilling the requirements needed for cable glands, a clear statement is needed that such devices have to fulfill the requirements that would be applicable to cable glands.

During the last meetings of IEC TC31 this problem was identified as a common concern for IEC 60079-0, IEC 60079-31 and IEC 60079-14. As such, this is an issue which should be solved quickly and so this DS is proposed. This issue will be clearly addressed by the next editions of IEC 60079-0, IEC 60079-31 and IEC 60079-14 but this may be some time away. In the meantime this DS is needed to avoid certification of such devices which may lead to unsafe installations.

QUESTION: Do all cable transit devices or similar entry devices need to fulfill the requirements for cable glands according IEC 60079-0 Clause 16 and Annex A and any other additional requirements in the applicable Type of Protection standards?

ANSWER:  Yes, the requirements for cable glands have to be applied to all cable transit devices or similar entry devices, where the cable(s) are designated to connect different Ex Equipment enclosures or to lead into an Ex Equipment enclosure.