- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

TITLE: Draft ExTAG Decision Sheet – Marking of combined Electrical/Non Electrical Equipment

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

Document, ExTAG/447/CD Draft ExTAG Decision Sheet - Marking of combined Electrical/Non Electrical Equipment, was prepared by INERIS and circulated to ExTAG for comment.  The Compilation of Comments, along with observations from the originator, are contained in ExTAG/469/CC.

This updated version, ExTAG/447A/CD Draft ExTAG Decision Sheet – Marking of combined Electrical/Non Electrical Equipment, takes into account the comments received and is issued for final discussion during the 2017 ExTAG Washington meeting.

Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: N/A | Clauses: N/A |  |
| --- | --- | --- |
| Subject: Guidance on marking requirements for combined electrical/non electrical equipment Status of document: Draft | Key words: - Marking - Labels | # Date: September 2017 Originator of proposal: INERIS |

Background:

Today the marking of electrical equipment is defined in IEC 60079-0 and the marking of non-electrical equipment is defined in IEC 80079-36.

Due to the fact, the combined marking is not defined in 60079-0 neither in

ISO 80079-36, the electrical part of the equipment has to be in accordance with IEC 60079-0 and the non-electrical part has to be in accordance with ISO 80079-36.

Therefore, the marking of electrical part and the non-electrical part has to be in two different lines:

- Ex db IIA T4 Gb

- Ex h IIA T4 Gb

QUESTION: How shall marking be shown for equipment covered by both the electrical and non electrical Standards (IEC 60079 and ISO 80079 series)

ANSWER:

After discussion with IEC TC31 Chairmen, SC31M Chairman and IEC TC31 WG22 it is decided to have combined marking for equipment which include an electrical part and a non-electrical part, for example:

- Ex db h IIA T4 Gb

- Ex h tb IIIC T135 °C Db

It will be clearer for the user that the combined risk of the electrical part and the non-electrical part has been performed for the complete equipment, stating one EPL, one Group and one T-Class for Gas and the same for Dust.

This will be written in the next edition of IEC 60079-0 and ISO 80079-36. An IEC/ISO Interpretation Sheet will be also prepared.

The Interpretation Sheet will also include a statement saying that non-electrical Ex Component does not have to be marked with a T-class.