- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Title:  ExTAG/536A/CD Revised Draft ExTAG Decision Sheet - ExTAG/536/CD Draft ExTAG Decision Sheet Suffix “X” and “U” to the certificate.

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

This document, ExTAG/536A/CD Revised Draft ExTAG Decision Sheet Decision Sheet Suffix “X” and “U” to the certificate has been prepared by SITIIAS/NEPSI, CN, taking into account comment received on ExTAG/536/CD, which it now replaces.

ExTAG/536A/CD is issued,  including track changes, in accordance with OD 035, for additional consideration over a six week period.

A Compilation of Comments on ExTAG/536/CD along with originator observations are contained in ExTAG/548/CC.

Please submit comments using the comments table, a separate document by –

2019 05 15

Christine Kane

Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-0:2011 IEC 60079-0:2017 IEC 60079-7:2015 | Clauses: 3.52, 3.53, 13,5, 29.9, 3.36, 3.83, 13.5, 3.84, 28.2 4.10 |  |
| --- | --- | --- |
| Subject: Suffix “X” and “U” to the certificate Status of document: Approved Draft | Key words: Ex component Suffix “X”, “U” | # Date: July 24, 2018 March 2019 Originator of proposal: SITIIAS/NEPSI |

Background:

With the extensive application of fieldbus, process control system adopts more and more power supply modules, remote IO modules and input/output modules etc.. It is popular that those modules have to be mounted into an additional housing and were tested according to IEC 60079-0 and IEC 60079-7 (former IEC 60079-15) as Ex component. So many Ex component certificates, with suffix “X” or “U”, have been issued already. It looks that each certification body have individual rule to apply suffix “X” or “U”.

QUESTION: For Ex ec components (power supply modules, remote IO modules and input/output modules), mounted completely in an Ex ec housing, suffix “U” or “X” shall be applied to the certificate?

ANSWER:

Suffix “ U” shall be applied on the those components, when they are evaluated individually and the temperature rise (both service and surface) shall be determined after installation in a suitable end product enclosure.

IEC 60079-0:2017 clause 3.84 has described that suffix “X” denotes Special Condition of Use for Ex Equipment. And IEC 60079-0:2017 clause 3.83 has described that suffix “U” denotes Schedule of Limitation for Ex components, which is incomplete equipment and not suitable for installation without further evaluation.

Those Ex ec modules shall be mounted into an Ex ec housing. The ingress of protection (IP) of the housing shall be tested according to IEC 60079-0 and IEC 60079-7. Because general industrial standards are not applied (IEC 60079-7:2015 clause 4.10.1 note). The mounting of modules shall be evaluated for the separation distance and temperature rise check etc..  All of above are critical factor for Ex equipment (housing+modules). So it is reasonable to define those modules are Ex component. And suffix “U” shall be applied to the IECEx certificate.

Note: When those components are tested for specific configuration (mounting, backboard etc..), certificate with suffix “X” may be issued for the whole system. In this case, the temperature test for the components shall be conducted when they are mounted as intended (for example, a family of PLC’s mounted on a DIN rail) and maximum service and surface temperatures shall be determined per IEC 60079-0.  The rated ambient temperature that is marked on the device shall be based on the temperature of the air surrounding the modules during this test.