- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Title:  Draft ExTAG Decision Sheet - Restricted installation requirements for Annex F

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

This document, ExTAG/549/CD Draft ExTAG Decision Sheet - Restricted installation requirements for Annex F has been prepared by UL, US, and is issued for consideration by ExTAG.

In accordance with OD 035 this document is issued for a six week comment period.

Please submit comments on this new Draft DS using the comments table, a separate document, by –

2019 05 22

to

Christine Kane

Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

- COLLECTION OF IECEx / ExTAG DECISION

| Standard: IEC 60079-11:2011 (Edition 6.0) IEC 60079-11:2006 (Edition 5.0) | Clause: 6.1.2.3 c) F.2 6.1.2 c) F.2 |  |
| --- | --- | --- |
| Subject: Restricted installation requirements for Annex F Status of document: Draft | Key words: - Annex F - Restricted installation | - Date: 2019 04 08 Originator of original proposals: UL Originator of this text UL TC/SC involved: MT 60079-11 |
| Background: When applying the reduced separation distances given in Annex F of IEC 60079-11:2011, there are three methods given to provide the protection to achieve pollution degree 2. One of the methods, as given in the following text, permits a restriction on the installation of the equipment to an area with the necessary pollution degree, in which case an IP20 enclosure is considered adequate protection for the equipment. (6.1.2.3 Apparatus complying with Annex F - excerpted) Apparatus meeting the separation requirements of Tables F.1 or F.2 shall be provided with protection to achieve pollution degree 2. This can be achieved by one of the following: c) an enclosure meeting the requirements of IP20 and by restricted installation, provided that the restricted installation requirements shall be specified as Specific Conditions of Use and the certificate number shall include the "X" suffix in accordance with the marking requirements of IEC 60079-0 and the Specific Conditions of Use listed on the certificate shall detail the installation requirements. (F.2 Control of pollution access - excerpted) Reduction of pollution degree 2 is achieved by: - (3rd dash) installation in a controlled environment with suitably reduced pollution; in such case the required condition of installation shall be added to the documentation provided by the manufacturer, and the symbol ”X” shall be added to the marking given in IEC 60079-0. Note: Comparable requirements exist in IEC 60079-11:2006 Clauses 6.1.2 c) and F.2. Question: Is it possible for portable equipment to use the “X” marking and restriction for installation in a pollution degree 2 environment in order to make use of the reduced separation requirements in Annex F? Answer: No, since portable equipment is not permanently installed but is carried on the person and moved from place to place it cannot be ensured that the equipment will always be located in an area that satisfies the pollution degree 2 requirement. |  |  |