- INTERNATIONAL ELECTROTECHNICAL COMMISSION (IEC) SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- Title:  Draft ExTAG Decision Sheet – Revision of ExTAG DS 2012/010 Medium for Documenting Required Instructions

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

During the May 2019 ExMC WG1 Meeting, held in Singapore, the topic of “Medium for Documenting required Instructions” was discussed in light of the current DS 2012/010 and latest technology. As a result of discussions it was agreed that DS 2012/010 should be updated to allow more flexibility.  UL, US, undertook to prepare a draft revision. The proposed changes to the current DS 2012/010 are shown in this revised document via the tracking tool.

This document is issued for consideration according to the OD 035. Please submit comments on this Draft DS using the comments table, a separate document, by –

2019 07 09

To

Christine Kane

Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-0:2011 IEC 60079-0:2007 | Clauses: 30 30 |  |
| --- | --- | --- |
| Subject: Medium for Documenting Required Instructions Status of document: Approved | Key words: - Installation - Instructions - Documentation - Medium - Electronic - Website | # Date: 2019 05 28 Originator of proposal: UL TC/SC involved: IEC/TC 31 |
| Question: When documenting the Instructions required by IEC 60079-0 (and the other IEC 60079 series standards), must these required Instructions be provided in paper format, or may they be provided in an electronic medium (such as CD, USB flash drive, URL or QRcode)? Answer: The documentation containing the Instructions required by IEC 60079-0 (and the other IEC 60079 series standards) may be provided by means of paper format alone, or by suitable electronic medium alone, or by both formats. Examples of suitable electronic medium for providing these required Instructions include a CD, USB flash drive, URL or QRcode. Where a URL is relied upon to provide required Instructions, there shall be marking on the apparatus that contains the international symbol (Reference No. 0434B of ISO 7000), along with the document number, revision level and URL location. This approach is consistent with how required Instructions can be addressed under relevant industrial standards. For example, see the IEC 61010-2-201 as just one example to consider. Whereas the IECEx System is able to take a flexible view on the form of the instructions, it should be noted that other constraints may apply in certain market places. In particular, it is noted that if an IECEx ExTR and/or QAR is to be used in support of claims of compliance with the ATEX Directive, the European Commission’s Standing Committee for the ATEX Directive have taken the view that at least the safety related parts of the instructions in respect of ATEX should be supplied in paper form, even if the wider operational Instructions are supplied in electronic form. |  |  |