INTERNATIONAL ELECTROTECHNICAL COMMISSION SYSTEM FOR CERTIFICATION TO STANDARDS RELATING TO EQUIPMENT FOR USE IN EXPLOSIVE ATMOSPHERES (IECEx SYSTEM)

- TITLE: Draft Decision Sheet - Enhanced clearance and creepage distances for equipment of Level of Protection “ec”

- Circulated to: ExTAG – IECEx Testing and Assessment Group

INTRODUCTION

This proposed Draft Decision Sheet was prepared by the IECEx Secretariat (in conjunction with IEC/TC 31 MT 60079-7, MT 60079-15 and AHG 47). It is issued for a one month period for consideration by ExTAG Members.

Please submit comments using the attached comments table by -

2016 04 25 to

Christine Kane

If there are no comments received the document will be forwarded for publication.

Julien Gauthier

Julien Gauthier

ExTAG Secretary

| Address: IECEx Secretariat Level 33 Australia Square 264 George Street Sydney NSW 2000 Australia Web: www.iecex.com | ExTAG Secretary Mr Julien Gauthier LCIE S.A. 33 Avenue du General Leclerc 92260 Fontenay-aux-Roses FRANCE Tel: +33 1 40 95 55 26 Fax: +33 1 40 95 89 37 Email : julien.gauthier@fr.bureauveritas.com |
| --- | --- |

| Member Body | Clause/ Sub-clause | Paragraph Figure/ Table | Type of comment General/ technical/ editorial | COMMENTS | Proposed change | Observation (to be completed by the originator) |
| --- | --- | --- | --- | --- | --- | --- |

COLLECTION OF IECEx / ExTAG DECISION

| Standard: IEC 60079-7:2015 (Edition 5.0) IEC 60079-15:2010 (Edition 4.0) IEC 60079-15:2005 (Third Edition) | Clauses: 4.3, 4.4.1 6.4 6.7 |  |
| --- | --- | --- |
| Subject: Enhanced clearance and creepage distances for equipment of Level of Protection “ec” Status of document: Draft | Key words: - Creepage - Clearance - Type of protection, “Gc” - Mains - Isolated circuits - Printed wiring board mounted components | - Date: 2016 03 xx Originator of proposal: IECEx Secretariat (in conjunction with IEC/TC 31 MT 60079-7, MT 60079-15 and AHG 47) TC/SC involved: IEC/TC 31 MT 60079-7, MT 60079-15 and AHG 47 Original Draft: ExTAG/xxx/CD |
| Background In IEC 60079-7:2015 (Edition 5.0), type of protection “nA” was transferred from IEC 60079-15:2010 to a new type of protection “ec”. As part of this transfer of requirements, two paragraphs on clearances and creepages were added to IEC 60079-7 for type of protection “ec” that were not in IEC 60079-15 for type of protection “nA”. See the last paragraph in Clauses 4.3 and the last paragraph in 4.4.1. These two paragraphs read when combined as follows; “Unless otherwise required in this standard, the enhanced clearance / creepage distances for equipment of Level of Protection “ec” only apply to mains circuits and between isolated circuits. The enhanced clearance / creepage distances do not apply to printed wiring board mounted components.” Based on the “Significance of changes” table in the Foreword of IEC 60079-7, these two paragraphs are only editorial clarifications between IEC 60079-15 and IEC 60079-7, and not extensions. Question What is meant by the following terms used in the last paragraphs in Clauses 4.3 and 4.4.1 of IEC 60079-7:2015: - “mains circuits” - “isolated circuits” - “printed wiring board mounted components” Answer The following provides clarification regarding what is meant by these terms: - the term "mains circuits" is intended to apply to circuits directly connected across the premise supply lines (sometime referred to as the “across-the-line” portion of primary circuits). - the term "isolated circuits" is intended to apply between a mains circuit and earth and between a mains circuit and any secondary circuit that is isolated from it (such as by an isolating transformer or opto-coupler). - The term "printed wiring board mounted components" is intended to apply to both the body of the component and to the solder points. Therefore, enhanced clearance and creepage distances required by Clauses 4.3 and 4.4 of IEC 60079-7 need only be applied as follows: - applied to the portion of the mains circuit that is directly connected across the premises supply lines, - applied between any portion of the mains circuit and ground, and - applied between any portion of the mains circuit and any secondary circuit that is isolated from it (such as by an isolating transformer or opto-coupler) It also noted that per 6.1 of the draft 7th edition of IEC 60079-0, “The requirements of this standard, together with one or more of the specific standards listed in Clause 1, are in addition to the applicable safety requirements of the relevant industrial standards.” This includes the relevant industrial clearance and creepage requirements. This Decision Sheet also applies to the clearance and creepage requirements in IEC 60079-15:2010 and IEC 60079-15:2005. |  |  |