COLLECTION OF IECEx / ExTAG DECISION

| Standard: IEC 60079-1:2014 (Edition 7.0) IEC 60079-15:2010 (Edition 4.0) IEC 60079-15:2005 (Third edition) | Clause: 15.5.2 22.4.1 33.4.1 |  |
| --- | --- | --- |
| Subject: Preparation of Flameproof, “dc”, and Enclosed-break, nC”, samples Status of document: Approved | Key words: - Flameproof, “dc” - Enclosed-break, “nC” - Preparation of samples - Enclosure - Thermal endurance - Tests of enclosures | - Date: 2015 05 07 Originator of proposal: UL LLC TC/SC involved: IEC/TC 31 MT 60079-1, MT 60079-15 Original Draft: ExTAG/368/CD |
| Background: Under the “preparation of samples” clause for both Flameproof, “dc”, and for Enclosed-break, “nC”, there is a Note indicating that non-metallic parts of the enclosure will have been subjected to thermal endurance testing. Question Consider a Flameproof, “dc”, device or an Enclosed-break, “nC”, device with the following characteristics: - Device incorporates a non-metallic body that houses the contacts. - Body of the device is to be fully housed within an overall enclosure in the end-application (therefore not exposed to any external mechanical abuses). For such a device construction, is the device required to be subjected to thermal endurance testing prior to the ignition/nontransmission test? Answers: Yes. As the body of the device is non-metallic, thermal endurance testing is required prior to the ignition/nontransmission testing because the type of protection depends upon the non-metallic body of the device for compliance with the ignition/nontransmission tests. Please note that if the body of the device also serves as an overall enclosure in the end-application, then the body also shall be subjected to the complete Tests of enclosures in accordance with IEC 60079-0. |  |  |