COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-14:2013 | Clauses: All as relevant | # Date: 2015 10 09 Originator of proposal: IECEx Secretariat + ExTAG Chairman |
| --- | --- | --- |
| Subject: Reference to IEC 60079-14 Explosive atmospheres - Part 14: Electrical installations design, selection and erection : 2013 (Edition 5) within an IECEx Certificate of Conformity or Unit Verification Certificate Status of document: Approved | Key words: Unit Verification installation assembly interconnection | Revised: DS 2015/001 TC/SC involved: TC31 Draft Decision Sheet: ExTAG/384/CD |
| NOTE: In accordance with Decision 2018/29 (ExMC/1436/DL), “the use of ExTAG DS 2015/001A (to) be withdrawn from use for IECEx Certification on 1st January 2020. After this date no Certificates can be issued based on DS 2015/001A.” Existing CoCs based on DS 2015/001A can remain active and be revised as needed in accordance with DS 2015/001A. Background: With the increasing need of industry to seek “proof of compliance” with safety standards being driven by a combination of regulatory requirements and vendor requirements imposed through supplier contracts, the IECEx Certified Equipment Scheme is being seen as an effective compliance tool in this regard. The need for a supplier of Ex equipment to provide proof of compliance includes at the Ex Component Level, finished Ex product and Assemblies of Ex products that come together in the form of functioning equipment. This Decision Sheet is intended to apply to an assembly of equipment or items of equipment that come together in the form of functioning equipment. It is not intended for assemblies considered to have complex design, or selection requirements or specific end user interfaces that maybe associated with clauses from IEC 60079-14:2013 such as: - Adverse conditions such as; vibration, heat, low temperatures, corrosion, chemical resistance. (clause 4.1) - Precautions related to switching of motors (clause 5.11.5) - Gas detection as a control measure (Clause 5.16) - Protection against external RF fields (clause 6.7.2) - Cathodic protection and interfaces to external CP systems. (clause 6.8) - Ex p systems where the entire Ex p system is not part of the assembly, I.e. some site interface is required to achieve the function. (clause 17.2.1) - Ex p for rooms, such as prefabricated buildings. (clause 17.4) such assemblies are regarded as an installation, nor is this Decision Sheet intended to apply to assemblies that contain their own source of explosion hazard for which additional considerations according to the IEC 60079-10 series may be required. IECEx provides the IECEx 03 Certified Service Facilities Scheme (covering activities related to the installation, inspection, maintenance, repair and overhaul of Ex equipment) and the IECEx 05 Certification of Personnel Competence Scheme (CoPC) for such applications. For main stream Ex Components and finished Ex equipment, usually mass produced, the IECEx 02 Certified Equipment Scheme provides for an IECEx Certificate of Conformity that requires: - Ex Test Report (ExTR) - Quality Assessment Report (QAR) - On-going Surveillance To deal with special items produced as “one-off” items or in limited quantities, IECEx provides for the issuing of an IECEx Unit Verification Certificate, according to IECEx Operational Document OD 033. The IECEx Unit Verification Certificate is also seen as a solution for providing evidence that all relevant requirements of the Installation Standard IEC 60079-14 have been met when dealing with Equipment assemblies. Note that certain “skid mounted” parts of plant, e.g. blending stations for fuel distribution, are a part of the plant and cannot be seen as equipment and therefore it is up to the end user to design the plant in accordance with the legal requirements (local installation requirements at the place of installation must be known and must be considered). It is further noted that IEC Technical Committee, TC 31 has established a working group TC 31/AHG46 to report to IEC TC 31 regarding the feasibility of producing a document that would permit certification of assemblies of equipment, for example skids. This ExTAG Decision Sheet is intended as an interim measure, until TC 31 produces a document, to provide guidance on the application of key aspects of IEC 60079-14 when being included in the overall assessment of assemblies of Ex equipment, to ensure a common approach is taken by ExCBs by defining a number of fundamentals that specify: - the minimum items that must be addressed during evaluation / assessment of Equipment assemblies - the information that must be included in both ExTRs and IECEx Certificates of Conformity (including Unit Verification) and how this must be presented NOTE: Where reference is made to IECEx CoC throughout this DS, this shall include - IECEx Certificate of Conformity - IECEx Component Certificate - IECEx Unit verification Certificate QUESTION: What are the requirements that must be fulfilled both by an ExCB and the Certification process, when incorporating relevant requirements of IEC 60079-14 into the IECEx Certificate of Conformity process when dealing with Equipment Assemblies consisting of different equipment and parts coming together as an assembly? ANSWER: Fundamental Requirements to be satisfied when incorporating relevant requirements of IEC 60079-14 into the IECEx Certificate of Conformity process include: Requirement No. 1: An IECEx CoC is associated with equipment according to the IEC 60079 or ISO 80079 series of Standards. If an item of equipment is out of the scope of the IEC 60079 series for electrical equipment or the ISO 80079 series for mechanical equipment an IECEx CoC cannot be issued. An IECEx CoC cannot be issued to show compliance with IEC 60079-14 alone. As a minimum, an IECEx CoC covering Equipment Assemblies must show compliance with the General Requirements Standard, IEC 60079-0, regarding assembly and interconnection of the items involved. Requirement No. 2: The “General Product Information” field of the ExTR supporting the IECEx CoC must clearly explain and detail the rationale of applying the various Clauses of IEC 60079-14 and clearly state which Clauses of IEC 60079-14 have been covered and the results of the relevant evaluations/tests. It is not possible to issue an ExTR for the installation of equipment in the end-users site. The latter may use IECEx Certified Service providers covered for this activity. Requirement No. 3: An IECEx CoC that includes reference to IEC 60079-14 shall state either within the IECEx CoC “Equipment” field, or as an attachment to the IECEx CoC, the specific Clauses of IEC 60079-14 that have been satisfied along with a schedule of Equipment including ALL items that comprise the Equipment assembly (including accessories such as entry devices, cable glands, blanking elements, breathing and draining devices) are to be listed within the IECEx CoC or as an attachment to the IECEx CoC with reference to the associated CoC number along with the relevant marking and identification of the applied standards, including the standard edition Requirement No. 4: ExCBs may only issue IECEx CoCs according to this decision sheet for Equipment Assemblies where the Ex protection techniques incorporated in the Equipment Assembly are covered under the ExCB’s scope of IECEx Acceptance. In line with the resource requirements of ISO/IEC 17025 and 17065, ExCBs and ExTLs shall identify within their organization those personnel that have been assessed as possessing the competence to evaluate the interconnection of parts according to IEC 60079-14. A completed scope extension declaration form, ExMC/251B/Q shall be completed by all ExCBs seeking to issue Unit Verification Certification according to this DS. In accordance with IECEx 02 rules and OD 009, IECEx Certified Equipment Scheme, Procedures for the Issuing of IECEx Certificates of Conformity, IECEx Test Reports and IECEx Quality Assessment Reports ExCBs, ExCBs can only accept applications for assemblies where the ExCB has all Ex protection techniques, associated with the Equipment Assembly, within their scope. Requirement No. 5: Items to be considered when evaluating Equipment Assemblies for compliance by an ExCB with the relevant requirements of IEC 60079-14 shall include, as a minimum: - That the applicant for IECEx CoC has clearly identified the EPL for the Equipment Assembly, along with the overall Group and T rating (including information on multiple EPLs), refer to IEC 60079-14 for relationship between EPLs and zones; - A Schedule of equipment, assembly drawings, wiring diagrams and other relevant information (such as IS calculations) that define the items of equipment and materials comprising the final Ex equipment assembly; - Items of Ex equipment that comprise the Equipment Assembly are to be covered by an IECEx CoC or shall be individually assessed by the ExCB and an IECEx CoC issued for that item; - The Ex protection of each item of Ex equipment comprising the Equipment Assembly shall be suitable for the declared EPL in item a) above; - The T rating of each item of Ex equipment and its Grouping comprising the Equipment Assembly shall be suitable for the overall declared T rating in item a) and Grouping; - Any completed cabling between individual equipment in the assembly shall be appropriate and in accordance with IEC 60079-14 and that it shall be provided with appropriate (and correctly assembled) cable entry devices. This shall be identified and recorded in the ExTR and Certificate to enable future maintenance. Note that cabling external to the assembly is not included; - Other requirements from IEC 60079-14 that are relevant to the particular equipment, for example that the mounting of flameproof enclosures takes account of the minimum obstruction distances for flange gaps in accordance with IEC 60079-14; - The final Equipment Assembly shall be provided with the required documents such as the instructions for use according to Clause 30 of IEC 60079-0; and - Ensure that all specific conditions of safe use/schedule of limitations of Certificates covering Ex equipment comprising the Equipment Assembly have been considered. Any residual conditions not fully complied with are to be detailed in the Equipment Assembly CoC for the end user to manage, including details concerning inspection. Details of the evaluation of the above items a) to h) shall be recorded in the ExTR as referenced within the IECEx CoC. Requirement No. 6: The Equipment Assembly shall be marked with, and the IECEx CoC shall mention, a single marking covering the complete assembly, including the symbol “Ex” and any important information regarding the safe use of the assembly, in addition to other mandatory requirements of the standard IEC 60079-0. For example : Ex IIC T4 Gb Tamb : -20°C to +85°C {Serial Number} {IECEx Certificate Number} along with a statement that the individual protection types are given in the marking and CoCs for the incorporated equipment. |  |  |