COLLECTION OF IECEx / ExTAG DECISIONS

| Standard: IEC 60079-7 Edition 4 | Clauses: 4.2.2.5 and 4.2.3.3 |  |
| --- | --- | --- |
| Subject: Mechanical Security of Soldered Connections Status: Approved | Key words: Soldered Connections | # Date: 2010.05.18 Originator of proposal: Baseefa TC/SC involved: 31 |
| Introduction This Decision Sheet applies to increased safety equipment where electrical continuity is made through a soldered joint. In ExTAG/158/CD issued April 2009, attention was drawn to potential ambiguity in the listed clauses in respect of the security of soldered connections for field wiring and factory wiring respectively. Although worded slightly differently, both clauses effectively require such a connection to be mechanically secure prior to the application of the solder. The response to the questions posed indicated that the views of ExCBs were divergent. The full set of comments was circulated in ExTAG/168/CC issued in July 2009, which included a proposal for an interim solution and that the problem should be passed to the Maintenance Team for IEC 60079-7 to find a solution. The ExTAG meeting in Melbourne agreed with the proposed course of action. MT 60079-7 met in Split during April 2010 and agreed that the wording was unclear. An ad-hoc WG has been set up to study the issue and report to MT 60079-7. It is anticipated that TC31 will then publish an ISH to IEC 60079-7. As it is therefore likely that it will be at least one further year before MT 60079-7 publishes the ISH, the decision was taken during the ExTAG Berlin 2010 Meeting, to publish this Decision Sheet as an Interim Document. Question. In respect of Mechanical Security, How are the clauses to be interpreted. Answer ExTAG is unable to give an authoritative answer and will await the output from TC31 MT 60079-7. Until such an answer is provided, the following should be considered as describing acceptable constructions: 1. Constructions where the electrical joint is fully functional and mechanically secure prior to the application of solder and the solder is merely used as a protection to exclude contamination 2. Constructions where the relationship between the two parts of the joint are rigidly defined by the mechanical construction, even if an electrical joint is not established, and the joint is completed electrically by the application of solder. In this sense, rigidly defined implies that were the two contact surfaces to just make contact, that contact would be maintained, without sparking, even in the event of vibration. |  |  |